# VOLUME 3

# TECHNICAL SPECIFICATIONS

GENERAL REQUIREMENTS

The Technical Specification is an integral part of the Tender Documentation /TD/ together with the provisions of the Contract, the detailed design drawings, building permissions and the other contract documents. The Specification specifies and further develops the requirements for the implementation of the construction works under the Contract.

Implementation of construction and assembly work must be consistent with all relevant execution of specific types of works legal and regulatory framework, technical rules and regulations and applicable standards following sequence and technology of the performance of different types of works in different parts of the site.

## Drawings, As-built Documentation and Operation and Maintenance Manuals

The contract Drawings are those listed in Volume 5, and those as shall be supplied under the Contract.

The As-built drawings and Operation and Maintenance Manuals shall be prepared in Macedonian languages.

The Contractor shall submit to the Supervisor, all the prepared documentation as well as all other guarantees and operation manuals for the installed equipment in three copies and in electronic format.

## Access to Site

The Contractor shall provide means of access to and on the site, for all personnel, materials and equipment.

For purposes of carrying out the Works, the Contractor shall limit his installations and operations to the defined working areas, as shown on the Drawings.

The Contractor if is necessary, shall submit for approval of the Supervisor and the relevant Authorities/Departments of the Republic of North Macedonia, details of his planned installations and operations at the sites defined on the Drawings as Contractor's working areas.

The Contracting Authority will provide free of charge a working area for the Contractor. The Contractor shall be responsible for the provision of suitable construction materials and for the construction of all-temporary offices, stores and workshops.

The Contractor shall provide a temporary fence to demarcate the working area and to provide a boundary during the construction period.

## Construction Generally

The following general requirements shall apply at each site:

- The Contractor shall provide and maintain all temporary roads, foot-paths and structures, necessary for the purpose of the Contract. On completion of the works, the Contractor shall remove such structures and restore the ground to the satisfaction of the Supervisor.

- The Contractor shall provide adequate lighting where work is being carried out and shall provide and install any additional lighting, which the Supervisor may require.

- The Contractor shall be responsible for the location of suitable sources of materials for the execution of the works, except where otherwise specified, whether such sources are on the site or not and for obtaining all necessary permissions.

- Materials available on the site shall be used for the execution of the works.

- Structures, which are to remain intact, shall be properly located, adequately supported, protected and maintained. Services shall be similarly treated, unless a diversion is deemed necessary, in which case it shall be carried out in a manner that prevents inconvenience to the owner and ensures the continuity and safety of the services concerned.

- The Contractor shall not pollute roads, lands and other places on the site.

- The Contractor shall provide and maintain adequate communications around the site.

- The Contractor shall provide, maintain and remove on completion of the works, fencing of the site and adequate security measures on access roads, but without prejudice to his obligations such as maintenance of free access for the Contracting Authority, the Beneficiary, the Supervisor and any other persons entitled to such access.

- As may be required by the Authority concerned, the Contractor shall be responsible for locating and protecting existing pipes, cables and other items of existing services and for the avoidance of damage to existing pavements and buildings, whilst they continue to be in use. In the event of the Contractor damaging water, fuel, electricity or telephone services, whether these have been marked out or not, the Contractor shall immediately inform the Authority concerned and advise the Supervisor.

The Contractor must keep a log at the construction site.  This log must contain all changes and deviations from the detailed design.  The construction log shall be signed and stamped by the Contractor and the Supervisor.

## Construction Program

In accordance with the Conditions of Contract, the Contractor shall submit to the Supervisor detailed programmes for the execution of the works, showing the order in which the various sections of the work are to be constructed, and in so shall take account of the restrictions and limitations described in this Specification.

Detail planning of working programme shall be agreed with the representative of the Contracting Authority.

Once accepted by the Supervisor, the programmes shall be strictly followed, unless any alterations are found necessary during the construction and confirmed by the Supervisor.

The Contractor shall state and allow a reasonable margin of time for the contingencies.

## Submissions to the Supervisor

Wherever these Specifications require, the Contractor shall submit to the Supervisor proposals, details, calculations, information, materials, test reports, certificates, etc. The Supervisor will consider each submission and shall reply to the Contractor in accordance with the relevant provision of the Contract Conditions.

No operation shall be carried out without complete notice having been given to the Supervisor by the Contractor, sufficiently in advance of the time of the operation to enable the Supervisor to make such arrangements as he may deem necessary for its inspection and checking.

The approval of the Supervisor of any submission shall not relieve the Contractor from his responsibilities under the Contract.

## Setting Out

The Supervisor will indicate to the Contractor sufficient primary reference points close to or on the sites, for the use by the Contractor in setting out the works. The Contractor shall set out the whole of the works relative to these points.

The Contractor shall protect the above reference points and level benchmarks, and in the event of damage shall survey and re-establish the points.

The Contractor shall set out the works in accordance with the Drawings supplied by the Supervisor, or as instructed by the Supervisor.

The Contractor shall verify all dimensions and levels shown on the Drawings and referred to in the documents forming of or issued under the Contract, on the site, and he will be held responsible for promptly pointing out errors in such dimensions and levels.

The existing reference benchmarks indicated by the Supervisor shall form the basis of measurement for all Construction works, unless otherwise requested in writing by the Contractor, or unless otherwise stated in the Contract Documents.

## Approval of sources, materials and plants

Materials incorporated must originate in a Member State of the European Union or a country covered by the Interreg - IPA CBC Programme 2021 – 2027. However, the goods to be purchased may originate from any country. Material that originates from sources, which are not approved by the Contracting Authority and the Supervisor, cannot be used for Works.

Approval of a source does not mean that all material in the source is approved. The Contractor has to ascertain by continuous control check measurements that only material which complies with the requirements specified in the various clauses of these specifications will be used for the Works.

## Weather Conditions

Without limiting his liabilities, the Contractor shall make suitable arrangements to protect the works and the temporary works, against the effects of the weather.

## Disposal of Materials

The Contractor shall not dispose of materials of any kind obtained from the site without the permission of the Supervisor. Debris shall be removed only to dumping areas approved by local authorities.

The Contractor must provide full compliance with the Rulebook on processing communal and other kinds of solid waste.

## Testing by the Contractor

The Contractor shall provide throughout the whole period of execution of the works, as requested by the Supervisor, all necessary tests for the control of the materials and workmanship, in accordance with this Specification. If necessary, the Contractor shall have such tests carried out by an independent organization, acceptable to the Supervisor.

## Safety on Site

Safety on site shall be a prime consideration of the Contractor who is to appoint a Safety Supervisor throughout the contract. This person is to provide the Supervisor with weekly reports on safety of all operations including regular inspection reports on all site equipment and the storage of hazardous materials.

The Contractor is to ensure that all persons working on the site are to have adequate personal protective clothing. He is also to provide the Supervision staff with helmets when visiting the site.

## Quality Assurance

The Contractor, his suppliers and other sub-contractors, shall comply with the Quality Standards set out in the Conditions of Contract, in all respects. Copies of the quality plan, records and other documentation, shall be submitted to the Supervisor, in respect to imported materials and before such materials arrive on the site.

## Liaison with CA

The Contractor shall keep in close contact with Contracting Authority Officials.

## Applicable standards

As a minimum the Macedonian standards and codes shall always be satisfied. Other internationally acknowledged standards and codes may be used only if:

- They are more or at least equally stringent compared to the respective Macedonian standards and codes or

- European technical approvals (with or without guidance).

The materials which are used must correspond to the requirements of the standardized documents asset in Macedonian standards and codes.

If the Contractor should wish to supply material or execute work to an alternative national standard or international specification, he shall give full details of his proposal in writing to the Supervisor.

## 1.17 Signs

The Contractor shall provide and maintain in good condition at least one project identification sign securely supported in a prominent location near to the access to the site. The signs shall be prepared strictly in accordance with the EU guidelines for Visibility.

  - CONTROL OF WORKS

The Contracting Authority will provide a consultant who will supervise construction with investment functions, according to Macedonian legislation and other legal acts in construction works. The Contracting Authority and / or Supervisor may at any time inspect the work, control technology performance and issue instructions to remove the defects, according to the specified technology and method of implementation. If found serious defects, errors and low-quality performance, the Contracting Authority shall notify the Contractor that breached the contract and should stop to work. The Contractor shall always provide access to the construction site of the authorized representatives of the Contracting Authority and the Supervisor.

2.1 Contractor's equipment

The Contractor shall furnish equipment which will be efficient and appropriate to secure a satisfactory quality of work and a rate of progress which will ensure the completion of the Works within the time stipulated in the Tender. If at any time such equipment appears to be inefficient, inappropriate or insufficient for securing the quality of work required or for the rate of progress, the Supervisor may be entitled to order the Contractor to increase efficiency, change the character or hire additional equipment, and the Contractor shall conform to such order.

2.2 Protection of existing structures and utilities

The Contractor shall assume full responsibility for the protection of all buildings, structures and roads existing in the area of the construction site, public or private, whether or not they are shown on the drawings.

The Contractor has to pay special attention to avoid any damages on any protected areas.

Any damage resulting from the Contractor's operations shall be repaired at his expense.

2.3	Safety and security on site

Safety and security arrangement should be performed in accordance with Macedonian Construction Law

2.4	Handling and storage of materials and plants

All materials and plants to be incorporated in the work shall be handled and stored in a manner which prevents injury of any kind whatsoever. Any materials or plants which, in the opinion of the Supervisor, have become too damaged to be fit for the use intended or specified shall be promptly removed from the site, and the Contractor shall receive no compensation for the damaged material or its removal.

2.5 Clean-up work

The Contractor shall clear way and remove from the site any wreckage, rubbish and temporary works, which are no longer required.

2.6	Responsibility of the Contractor

Approval from the Supervisor does not relieve the Contractor from his obligations or responsibilities under the Contract.

3.	ADMINISTRATIVE SPEIFICATIONS.

3.1 Progress meetings

The Contractor shall agree with the Supervisor and the Contracting Authority for dates for regular progress meetings. These meetings shall normally be held monthly, no later than 10 working days after the completion of each month.

3.2 Quality assurance

The Contractor shall institute a quality assurance system to demonstrate compliance with the requirements of this contract. The system shall be in accordance with the details stated in the Contract. The Supervisor shall be entitled to audit any aspects of the system.

4.	IMPLEMENTATION OF THE WORKS

4.1	Materials

The Contractor shall use only materials that conform to the technical requirements set forth in the clauses of this Technical Specification.

All Materials and Plant supplied to perform the Permanent Works under the contract shall be new products. Second-hand Materials and Plant will not be accepted.

The Tender drawings constitute the drawings issued for construction/ installation/ execution.

4.2	Testing

Reliable shall be only the type and number of tests performed in conformity with the prescription of this technical specification, except when this right is granted to the Contracting Authority.

The Contracting Authority may require additional tests when the results obtained are uncertain.

Besides the tests specified in this Specification, the Contracting Authority may require additional tests to establish possible hidden omissions and effects. Costs for these tests shall be entirely at the Contractor’s expense if such defects are confirmed.

4.3	Inspection and measurement of works

The Contracting Authority may at any time inspect the quality and measure the amount of work performed. If this cannot be done with the Contractor’s assistance, a deadline shall be fixed for hiring external specialists. In this case, the expenses shall be paid by the Contractor.

5.	PREPARATORY WORKS

Before starting the works the Contractor has to perform some preparatory works at the site.

5.1	Boards and signs

The Contractor shall mount and maintain in good condition a board with the name of the project and the co-financing institutions written in a way /text and font size/ conforming to the requirements of the Contract and in compliance with EU visibility guidelines.

5.2 Setting out the site

The Contractor shall in co-operation with the Contracting Authority set out the total site to be used for construction.

5.3 Temporary facilities

The Contractor shall effects all expenditure for establishing, operation and removal of temporary facilities if such are needed for the good performance of the Contract. All needs for establishing such facility shall be duly justified.

5.4 General supply facilities

###### Sanitary Arrangements

The Contractor shall provide for and maintain temporary sanitary facilities on the site for the use of all persons connected with the Works. The Contractor shall keep the facilities in a clean and sanitary condition and shall post notices and take such precautions as may be necessary to keep the site clean.

###### Water supply

The Contractor shall provide for and maintain an adequate supply of potable water for his use. The water supply shall be used for construction purposes and for consumption in the temporary facilities.

###### Power supply

All electrical power required by the Contractor shall be provided by him at his own expense. The Contractor prior to taking-over of the Works shall remove all temporary installations if it is not agreed upon that the Contracting Authority takes over the installations.

6. ADDITIONAL SPECIFICATIONS

All provisions and clauses from the Macedonian Construction Law and other codes that are valid obligate the Contractor.

SPECIFIC REQUIREMENTS

Establishing a multipurpose recreation playground around Lake Gradche

Architectural program and design

The field has a simple rectangular shape with dimensions of 42.10m x 25.10m. The field should preferably be placed on the NORTH-SOUTH axis with its longer side. The main and only entrance is placed on the longer side. It consists of recreational fields for small football, handball, and basketball with all accompanying elements such as benches and rest tables, a referee's chair, four baskets, two goals, and lighting. The fence that encloses the playground is 4 meters high on the longer sides and 5 meters on the shorter sides.

Total area of the site 42,1х25,1m .......................................................... 1056,70 m²

Total area (including surrounding pathway) 42,1х25,1m ..................... 1296.75 m²

Preparatory work

Prior to commencing earthworks for the construction of the multi-purpose recreational playgrounds, the site will be cleared of trees, low vegetation, various substrates, etc.

Earthworks

The earthworks will be conducted in accordance with applicable regulations, ensuring proper excavation safety measures. During excavation, there will be a separation of excavated soil with stronger deformable characteristics (gravel and sand) from those with weaker characteristics (topsoil, dust, and clay). The soil with better characteristics will be used for backfilling around the foundations.

Excavation will be performed mechanically to a depth of 0.43 meters below the top level of the asphalt surface. The remainder of the excavation under the foundation strips and individual foundations will be done manually. The trench for drainage installation will be excavated narrowly using machinery.

Reinforced concrete works

The reinforced concrete works will be carried out using ready-mixed concrete MB30 with formwork. Strip footings and isolated footings for the lighting poles and goal posts will be constructed with formwork. All reinforced concrete works up to level 0.00 will include an additive for concrete waterproofing (HYDROFOB 05).

A lean concrete layer d=10cm and gravel d=20cm will be placed under the strip footings. Under the isolated footings, a lean concrete layer d=10cm and gravel d=30cm will be placed.

Ground surface preparation

The ground surface preparation is conducted in accordance with the site conditions.

-Asphalt AB8, thickness 3cm

-Asphalt BNS22, thickness 5cm

-Subbase, thickness 35cm – crushed stone 0-63mm, bearing capacity up to 70 MN/m²

-Geotextile

-Subsoil levelled and compacted to a bearing capacity of 35 MN/m²

Asphalting is performed in two layers. First, a layer of asphalt with a thickness of 5cm and granulation BNS 22 is laid. Then, a layer of asphalt with a thickness of 3cm and granulation AB 8 is applied.

Drainage

The terrain slopes on two sides. According to program requirements, perimeter drainage with inspection shafts with metal covers will be installed for drainage purposes. Placement of the drainage will be done in accordance with the supervisory authority. For surface water drainage where no drainage is installed, channels will be provided.

Fencing

The playgrounds will be enclosed with wire mesh - universal steel-plastic-coated weave set in a system of steel vertical posts 100/80/4 and horizontal barriers 80/40/3, galvanized and painted dark green. The fence height is 5m on shorter sides (behind the goal structure) and 4m on longer sides (behind the basketball structure). The fence will include steel box-profile gates with a universal steel-plastic-coated weave infill and lock. Above each gate, a lighted advertising board with dimensions 200/80 cm will be installed. A surrounding concrete pathway is planned around the fence. No other accompanying structures are envisaged within the site.

Equipment

The site will feature 2 goals for recreational small football and handball, standard for their purpose, and 4 basketball hoops mounted on steel profiles Ø133. Additional equipment includes benches for resting and for visitors. The equipment-furniture must be made from durable materials (steel or aluminium).

A waste bin will be fixed to one of the fence posts. Lighting will be provided with floodlights mounted on 4 steel poles, each 12m in height, to accommodate evening use of the site. Electrical connection for the site will be facilitated according to local authorities' regulations.

Additionally, procurement of two four-person pedal boats is planned.

The design of the structural part of the aforementioned facility was developed in accordance with:

- The investor's request;

- Applicable standards and regulations according to the 1987 BAB rulebook;

- Data on multipurpose playgrounds, geometry and dimensions;

- Architectural bases from which the basic parameters for the preparation of the project documentation were taken;

- The design includes a reinforced concrete structure - foundations and steel, main and secondary construction.

The geometry of the same is adopted, both from an architectural aspect for the needs of the investor, and from the min. dimensions for the function of the facility.

The steel structure of box profiles, anchors and anchor plates includes a fence for the playgrounds, as well as an appropriate mesh of universal knitting for which details are provided in the appendix. Also, the poles for electrical installation - reflector supports are made of steel with a variable circular cross-section, anchors and anchor plates. The holder for the selected type of lamps is placed at the upper end of the steel pole. Details are given for the steel structure of the basket with anchors and anchor plates. The static analysis was performed in accordance with the regulations for the construction of objects of this type with a sophisticated computer program package SAAP 200n for horizontal and vertical loads, according to the applicable regulations. All structural elements are designed for concrete MB30, reinforced with RA - 400/500, both for the single foundations for reflectors and basket, and for the strip foundations for the fence. The foundation will be carried out according to the conditions of the existing location and the bearing capacity of the soil. The dimensioning of the foundations was performed at the permissible bearing capacity σ doz. = 150 kpa, which is taken conditionally. If during the excavation a different bearing capacity is determined from the assumed one, a Geomechanics expert should be consulted in order to accept the construction pit. A buffer of 30 cm and 10 cm of lean concrete is provided under the foundations, under single foundations, and a buffer of 20 cm and 10 cm of lean concrete under foundation strips.

1.1- Luminaires

A. Luminaires (Lamps): In accordance with EN standard 12193, or with another equivalent standard, IEC, DIN- i.e. with optical systems that will allow optimum performance in lighting the playgrounds. The optical system shall be made of anodized aluminum with a high degree of reflection for horizontal alignment as a wide beam projector. The luminaire shall be of asymmetric medium wide angle, with a vertical light distribution of 65 °.

B. Aluminum reflectors: Made of cast aluminum housing with a thickness of not less than 0.7 mm. The reflector fixing part shall be made of galvanized steel, continuously adjustable, and suitable for mounting the projector in an upright and angled position. The cover shall be made of tempered safety glass, sealed with silicone sealant and with stainless steel connectors.

Surface exposed to wind Av = 0.187 m2, and a defined reflector weight of 20 kg.

C. Electrical connection via a connector integrated into the igniter with a 4-pole terminal up to 2.5 mm2 and a cable gland for a line up to 6-12 mm in diameter. Given the category of the local type playground, an igniter with instantaneous ignition is not provided.

D. Electronic ballasts and two capacitor banks per reflector to be placed in the RO-4 switch cabinet.

1.1.1- Metal Halide Lamps: Consisting of a quartz tube enclosed in an outer transparent housing, they operate on the same principle as all tubular lamps with iodide gas additives, such as indium, thallium and sodium, in mercury tubular lamps, to increase the intensity in the three spectral bands, i.e. blue, green and yellow-red with high colour intensity. The lamps shall be equipped with an electronic ballast. The lamps shall comply with IEC 60188. The guaranteed average life span shall not be less than 10,000 hours, i.e. the illumination after 100 hours of operation shall be in accordance with the following list: 1. 90,000 lumens for 1,000 W lamps 2. 190,000 lumens for 2,000 W lamps

The permissible temperature of the base should not exceed 250°C, and the maximum temperature of the lamp itself should not exceed 550°C. Lamps with an intensity of 1000 W, and a voltage of 220 V should be able to operate in a position up to 65 degrees.

1.1.1- Poles

The poles are planned to be made of steel cylindrical pipes, dimensioned for a wind speed of 110 km/h. The poles are protected from corrosion and painted silver.

The installation of the poles is planned in concrete foundations with dimensions presented in the attached detail in the project.

The fastening of the poles to the foundation is carried out with anchor bolts M20×600mm (which are placed in the foundation during the concreting phase) and an anchor plate using an M20 nut.

Consoles with a length of 1.6m are installed on the poles. The total height of the pole with the console from the field level to the lamp is ~12.8m.

A galvanized M8x35 screw with a nut on each pole is provided for grounding the poles.

NOTE: The poles, according to the input data from the Electrical Project, are processed in the Basic Project for Lighting of Multipurpose Playgrounds - Electrical Phase

1.1.2 - Field Lighting

For the defined competition classes, local type (illumination level 200Lx) and type of competition, the Photometric calculation for field lighting was performed. It was made using the software program "Dialux". The dominant factors that define the quality of lighting for good uniformity are the ratio Emin/Emax; Emin/Em and uniformity Uо. By achieving these conditions, uniformity in lighting is ensured. For quality uniformity, this ratio must be min. 0.33.

The photometric calculation is made with a software program for a specific type of lamp, the same lamps are specified in the bill of quantities with their lighting characteristics that guarantee the obtained results for brightness level and uniformity. Any replacement of the planned lamps with others from the same or another manufacturer requires checking their lighting characteristics, i.e. presenting results with the appropriate photometric calculation.

For duty lighting, it is planned to install a reflector with metal halide lamps with a power of 400W, placed at 8m, controlled manually and automatically using a photo relay.

1. 2- Low voltage cables

This section includes conductors, cables and connectors for power supply systems. Conductors, cables and connectors in the project are used:

1. In electrical circuits for power distribution.

2. In electrical circuits for lighting.

In general, the following applies to conductors and cables:

In general, all power cables of external cable distribution are laid in earth trenches.

The cables should have stranded copper conductors (4 mm2 or more), based on IEC 60228 Class 2.

Cables that are directly buried in the ground should be armored cables, cables insulated with steel tapes and protected by concrete slabs and warning tapes. When directly buried cables pass under pavements, pipes or other similar services, then they should be placed in pipes filled with a quantity of PVC sufficient to withstand the more extreme conditions. In no case should cables be buried directly in concrete, bricks or stones or floor finishes. Cables should be colour coded or otherwise identified in accordance with the regulations for the application of voltage systems. The construction of the insulation of the wires should be as follows:

Brown and black for phases (1, 2, 3).

Blue for neutral.

Green/yellow for earth.

Phase conductors whose sheath is not colour coded shall be marked with alphanumeric characters (L1, L2, L3) or shall be colour coded on insulated tapes.

Conductor Plain, annealed electrolytic copper or aluminum conductors, solid circularly stranded, complying with the requirements of IEC 60228.

Insulation PVC based thermoplastic or XLPE thermosetting material, complying with the requirements of EN 60502-1. Structure - the insulated conductors are arranged and compacted in a circular shape next to each other, filled with non-hygroscopic material (where necessary) and covered with an additional layer of thermoplastic material or non-hygroscopic bonding tape.

Sheath - PVC based thermoplastic material, complying with the requirements of EN 60502-1.

The power cables and conductors must be in accordance with DNI VDE 0276-603 (HD 603.1) type 3G-2; DIN VDE: 0250/204; DIN VDE: 0281-3 (HD 21.3) and must have certificates for the raw materials from which they are made and for the cable as a finished product according to IEC 60502-1.

1.3- External cable cabinets RO

This specification includes external cable cabinets for power supply and lighting control of Multipurpose Playgrounds.

External cabinets with a nominal voltage of 600V and lower are identified as RO and have the following parameters.

- Nominal voltage 400/230V

- Nominal insulation voltage 1000V

- Nominal frequency 50Hz

- Nominal short-circuit current 1s 36kA

- Nominal peak current up to 50 kA

- Main earthing bus TN-C/S

- Degree of protection IP55

- Auxiliary control voltage 230V AC

The cabinet will be completely standardized, with a hinged door with the necessary ventilation controlled by a thermostat adapted to quickly remove the heat generated by the components. The distribution cabinet will have a reserve space of 20% more than the prescribed respective single-pole schemes.

I.3.1- Components and functionality

The distribution board units must be from the same manufacturer. All devices will be mounted on guide or fixed plates and on specific cross-beams. Welding will not be allowed. The connections of the control circuits will be guided in plastic pipes section adapted to the quantity of cables it contains. The conductors of these circuits will have the same cross-section as the cables of the power circuits, never with a smaller cross-section or grouped with a smaller cross-section. The conductor will be identified by the ring number according to the identification of the functional drawing. All mounted electrical and electronic components must have an identification that corresponds to that in the electrical drawings.

The cabinet is intended to accommodate the ballasts, fuses and cam switches for automatic and local control of the light.

I.3.1- Test

The built-in elements in the Distribution Cabinet should have a type test report and be in accordance with the applicable IEC and European EN norms and standards, namely: EN 60044-1; EN 60255; EN 60439; EN 60529; EN 60695; EN 60947. The manufacturer of the Cabinet should provide confirmation of its functionality.

1. 4 - Power supply

The connection point for the power supply of the distribution cabinet P0-4 will be defined in accordance with the electrical permit.

NOTE: EVN defines the connection point and measurement. The project documentation defines a power cable from the connection point to the distribution cabinet with an orientation length of up to 60m. For distances greater than 60m - additional calculations should be performed. The connection is planned to be made with a cable type NAYY- 4×25mm2 in a trench in the ground with dimensions 0.40.8m. A galvanized strip 35x4mm is laid parallel to the cable for performing the grounding of the poles. A plastic warning tape "CAUTION, POWER CABLE" is laid above the cable in the trench at a vertical distance of 40cm.

II. Grounding of the fence

To protect the fence from atmospheric discharges, grounding is planned. Grounding is carried out with a galvanized strip FeZn 35×4mm, laid in a trench in the ground at a distance of 2m. The fence is connected to the grounding conductor - with a galvanized strip FeZn 35x4mm.

TECHNICAL CONDITIONS FOR LAYING CABLES

- Laying cables is usually done freely in the ground, in a previously dug trench. The dimensions of the trench in the ground (on sidewalks and ground surfaces) are as follows: The depth of the trench is 0.8m, and the width depends on the number of cables that are laid in parallel in the trench. The layout with the dimensions of the trench, for various cases of laying cables is given in the attached drawings.

- At crossings over streets, roads and paths, as well as in all those places where greater mechanical stresses on the ground can be expected or there is a possible possibility of mechanical damage to the cable, the cable is exclusively laid in cable ducts made of concrete blocks with an opening diameter of 100 mm or plastic pipes.

- In the dug trench, a layer of sifted soil is first placed, and the cable is laid on it. After the cable position has been recorded, a second layer of sifted soil is placed, 10 cm thick. Above the second layer of sifted soil, the trench is backfilled with excavated soil up to 40 cm above the cable. The soil is poured in layers of 10-15 cm and well compacted. At a height of 40 cm above the laid cable, a plastic warning tape is laid along the entire length of the cable route. The remaining 30 cm of the trench is backfilled with excavated soil, in layers of 10-15 cm and well compacted, taking care not to bend the tape. - The cable must be bent with a slight curve whose radius must be at least 15 D, where D is the outer diameter of the cable. - The cables must not be laid at a temperature lower than 0° C. It is recommended that the cables be laid at an outdoor temperature above +5° C.

- When laying multiple cables in the same trench in parallel, the distance between them must be at least 10 cm between 1 kV cables, 15 cm between 1 kV and 10 kV cables.

- The mutual crossing of the cables must be carried out with a distance of at least 10 cm.

- If there are existing electric cables along the designed route, before digging the trench, transverse trenches should be dug to determine the route of the existing cables.

- When laying and crossing power cables in parallel with other underground utility installations, the prescribed distances should be observed. Since there are only regulations for parallel laying and crossing of power cables with power connection cables - TT cables, for parallel laying and crossing of power cables with other underground utility installations we use some practical experiences and regulations that are valid in European countries, as well as the draft rulebook on technical measures and conditions for the use of power cables.

- When laying power cables next to power connection cables - T-T cables, the following prescribed distances for protecting T cables from the influence of power cables, provided for in the official journal of the SFRJ No. 34/51, 6/52 and 13/60:

- Power cable of 1 kV next to the cable for electrical connection min 0.3 meters;

- Power cable of 10 kV next to the cable for electrical connection min 0.5 meters;

- Power cable above 10 kV next to the cable for electrical connection min 1.0 meters.

In case the specified distances cannot be achieved, the power cables should be laid in a pipe with good conductivity (steel pipe), and for electrical connection in a pipe with as little conductivity as possible (concrete pipe) or a protective channel made of similar material.

The metal sheath of power cables for voltages greater than 250V, in the section of parallel laying, must be grounded at least at each joint, and for power cables above 10 kV the distance between individual grounding conductors should not exceed 200 m in the section of parallel laying of the cables. The earthing conductor should be at least 2 meters away from the power cable.

- The intersection angle should generally be as close to 90° as possible but must not be less than 45°, except in special cases it can be smaller but not less than 30°

- The horizontal distance of 10 kV power cables with the power cable must be at least 50cm. If this distance cannot be achieved, then the power cable is placed in a 2-3m long metal pipe, and the power cable in a concrete pipe, so that the distance in this case must not be less than 30cm.

- All intersections of power cables with underground utility installations are considered as places of probable mechanical damage to the cables, which is why additional protection of the cables from mechanical damage is installed at these places.

- Parallel laying of cables next to pipelines and hot water pipes should be avoided in most cases, otherwise the following distances must be achieved:

  - When laying a cable parallel to a water pipe: 0.5m minimum

  - When crossing a cable with a pipeline of lesser importance: 0.3m minimum

  - When crossing a cable with a main pipeline: 0.5m minimum.

  - In all the above cases, the cable should be mechanically protected.

- The distance between the cable and the hot water pipe when crossing must not be less than 0.6 meters. In addition, the hot water pipe on the crossing section, 2 meters on both sides, must have such thermal insulation that the ground temperature does not increase by more than 10°C at the highest summer temperature and no more than 15°C at the lowest winter temperature.

- Horizontal distance between power cable and heating pipe during parallel routing-laying must not be less than 30cm, 70cm or 150cm.

- The intersection of cables with traffic lanes is carried out at a depth of 1.10-1.50m under the roadway, depending on the number of concrete blocks.

- The cable is laid in concrete blocks or steel pipes with an internal diameter according to the external cross-section of the cables, i.e. ф100mm and ф160mm. The concrete blocks should protrude 1m beyond the edges of the roadway.

- The connection of cables shall be made with connectors according to the cross-section and type of cable, and in accordance with the JUS regulations, the manufacturers' instructions and the requirements of "Electro Skopje".

- The manufactured connectors must not be buried until they are taped.

- The cable terminations shall be made depending on the location and type of cables.

- Plates shall be placed on the cable terminations with markings of

- the characteristics of the cable, type and type of cable, cross-section and voltage.

- The cable outlet on the pole shall be protected with an iron pipe.